## README
Heating System Design for a Residential Building
Authors: Alessandro Capodacqua, Gabriele De Stalis
Course: Sperimentazione e Progettazione di Tecnologie Energetiche - Politecnico di Torino (A.Y. 2025-2026)
Supervisor: Prof. Carlo Cima
This workbook consolidates the calculation tables from the original technical report into
formatted spreadsheets, grouped by topic (one sheet per calculation area).
Sheets:
- Building Envelope: wall/floor stratigraphy, opaque & glazed surfaces, attic, basement, ventilation & thermal bridges
- Total Loads: per-room and whole-building thermal load summary
- Distribution Network: radiator reference data and pipe sizing
- Pump Head: distributed & localized head losses, pump selection
- Heat Generator: generator selection and performance
- Chimney Sizing: flue gas flow rates, geometry, draft verification
- Sources: standards and manufacturer data sheets used
Note on data fidelity: values are transcribed directly from the original report. A few
subtotal rows in the original are labeled kW where the order of magnitude suggests W was
intended (a units slip in the original spreadsheet export); these are flagged in a Note
column rather than silently corrected.

## Building Envelope
Opaque Wall - Stratigraphy
layer number | layer name | thickness m | conductivity W mK | resistance R m2K W
1 | Internal plaster (lime and gypsum) | 0.015 | 0.7 | 0.021
2 | Load-bearing brick block (heavy) | 0.25 | 0.27 | 0.926
3 | Insulation panel (XPS) | 0.08 | 0.031 | 2.581
4 | Unventilated air gap | 0.04 |  | 0.18
5 | Hollow brick (light protective layer) | 0.08 | 0.27 | 0.296
6 | External plaster (lime/cement) | 0.015 | 0.8 | 0.019
| TOTAL | 0.48 |  | 4.023
Opaque Wall - Total Transmittance
parameter | value | unit
Total wall transmittance U | 0.238 | W/m2K
Internal surface heat transfer coefficient alpha_int | 7.78 | W/m2K
External surface heat transfer coefficient alpha_ext | 22.5 | W/m2K
Opaque Surfaces - Heat Dispersion by Room
apartment group | room | floor area m2 | external wall area m2 | opaque area m2 | exposure coeff | phi op W
North central | Living room | 29.19 | 6.56 | 3.41 | 1.2 | 27.2
North central | Kitchen | 11.25 | 6.56 | 4.31 | 1.2 | 34.4
North central | Bedroom 1 | 10.76 | 7.7 | 5.45 | 1.2 | 43.6
North central | Bedroom 2 | 13.65 | 7.7 | 5.45 | 1.2 | 43.6
North central | Bathroom | 10.76 | 0 | 0 | 1 | 0
North central | TOTAL | 75.61 | 28.52 | 18.62 |  | 148.8
North central | TOTAL x2 |  |  |  |  | 297.6
South central | Living room | 29.19 | 6.56 | 3.41 | 1 | 22.7
South central | Kitchen | 11.25 | 6.56 | 4.31 | 1 | 28.7
South central | Bedroom 1 | 10.76 | 7.7 | 5.45 | 1 | 36.3
South central | Bedroom 2 | 13.65 | 7.7 | 5.45 | 1 | 36.3
South central | Bathroom | 10.76 | 0 | 0 | 1 | 0
South central | TOTAL | 75.61 | 28.52 | 18.62 |  | 124
South central | TOTAL x2 |  |  |  |  | 248
South-East / South-West | Living room | 31.62 | 7.02 | 3.87 | 1.15 | 29.7
South-East / South-West | Kitchen | 11.19 | 7.97 | 5.72 | 1.15 | 43.8
South-East / South-West | Bedroom 1 | 11.19 | 7.97 | 5.72 | 1.15 | 43.8
South-East / South-West | Bedroom 2 | 12.43 | 19.36 | 17.11 | 1.1 | 125.4
South-East / South-West | Bathroom | 10.76 | 0 | 0 | 1 | 0
South-East / South-West | TOTAL | 77.19 | 42.32 | 32.42 |  | 242.7
South-East / South-West | TOTAL x2 |  |  |  |  | 485.4
North-East / North-West | Living room | 31.62 | 7.02 | 3.87 | 1.15 | 29.7
North-East / North-West | Kitchen | 11.19 | 7.97 | 5.72 | 1.2 | 45.8
North-East / North-West | Bedroom 1 | 11.19 | 7.97 | 5.72 | 1.2 | 45.8
North-East / North-West | Bedroom 2 | 12.43 | 19.36 | 17.11 | 1.15 | 131.1
North-East / North-West | Bathroom | 10.76 | 0 | 0 | 1 | 0
North-East / North-West | TOTAL | 77.19 | 42.32 | 32.42 |  | 252.4
North-East / North-West | TOTAL x2 |  |  |  |  | 504.8
Opaque Surfaces - Total Dispersion
parameter | value | unit | note
Total opaque surfaces dispersion | 1535.8 | kW | as reported in original report - order of magnitude suggests this may actually be W; kept as in source, verify before reuse
Glazed Surfaces - Heat Dispersion by Room
apartment group | room | base area m2 | window width m | window height m | window area m2 | exposure coeff | phi glazed W
North-West / North-East | Living room | 31.62 | 1.5 | 2.1 | 3.15 | 1.15 | 64.9
North-West / North-East | Kitchen | 11.19 | 1.5 | 1.5 | 2.25 | 1.2 | 48.4
North-West / North-East | Bedroom 1 | 11.19 | 1.5 | 1.5 | 2.25 | 1.2 | 48.4
North-West / North-East | Bedroom 2 | 12.43 | 1.5 | 1.5 | 2.25 | 1.15 | 46.4
North-West / North-East | Bathroom | 10.76 | 0 | 0 | 0 | 1 | 0
North-West / North-East | TOTAL | 77.19 |  |  | 9.9 |  | 208.1
North-West / North-East | TOTAL x2 | [5 empty] | 416.2
South-West / South-East | Living room | 31.62 | 1.5 | 2.1 | 3.15 | 1.15 | 64.9
South-West / South-East | Kitchen | 11.19 | 1.5 | 1.5 | 2.25 | 1.15 | 46.4
South-West / South-East | Bedroom 1 | 11.19 | 1.5 | 1.5 | 2.25 | 1.15 | 46.4
South-West / South-East | Bedroom 2 | 12.43 | 1.5 | 1.5 | 2.25 | 1.1 | 44.4
South-West / South-East | Bathroom | 10.76 | 0 | 0 | 0 | 1 | 0
South-West / South-East | TOTAL | 77.19 |  |  | 9.9 |  | 202.1
South-West / South-East | TOTAL x2 | [5 empty] | 404.2
South central | Living room | 29.19 | 1.5 | 1.85 | 2.78 | 1 | 56.4
South central | Kitchen | 11.25 | 1.5 | 1.5 | 2.25 | 1 | 40.3
South central | Bedroom 1 | 10.76 | 1.5 | 1.5 | 2.25 | 1 | 40.3
South central | Bedroom 2 | 13.65 | 1.5 | 1.5 | 2.25 | 1 | 40.3
South central | Bathroom | 10.76 | 0 | 0 | 0 | 1 | 0
South central | TOTAL | 75.61 |  |  | 9.53 |  | 177.3
South central | TOTAL x2 | [5 empty] | 354.6
North central | Living room | 29.19 | 1.5 | 2.1 | 3.15 | 1.2 | 67.7
North central | Kitchen | 11.25 | 1.5 | 1.5 | 2.25 | 1.2 | 48.4
North central | Bedroom 1 | 10.76 | 1.5 | 1.5 | 2.25 | 1.2 | 48.4
North central | Bedroom 2 | 13.65 | 1.5 | 1.5 | 2.25 | 1.2 | 48.4
North central | Bathroom | 10.76 | 0 | 0 | 0 | 1 | 0
North central | TOTAL | 75.61 |  |  | 9.9 |  | 212.9
North central | TOTAL x2 | [5 empty] | 425.8
Glazed Surfaces - Total Dispersion
parameter | value | unit | note
Total glazed surfaces dispersion | 1600.8 | kW | as reported in original report - order of magnitude suggests this may actually be W; kept as in source, verify before reuse
Window - Technical Specifications
parameter | value | unit
Model | Winergetic Premium Passive (Oknoplast)
Glass transmittance Ug | 0.3 | W/m2K
Window transmittance Uw | 0.6 | W/m2K
Acoustic insulation | 33 | dB
Glazing | Quadruple low-emissivity + argon gas
Floor - Stratigraphy
layer number | layer name | thickness m | conductivity W mK | resistance R m2K W
1 | Ceramic tiles | 0.01 | 1.3 | 0.0077
2 | Concrete screed | 0.05 | 1.3 | 0.0385
3 | Insulation (Polyurethane) | 0.08 | 0.028 | 2.8571
4 | Hollow-block floor slab | 0.2 |  | 0.25
5 | Internal plaster (basement side) | 0.15 | 0.8 | 0.1875
| TOTAL | 0.49 |  | 3.3408
Floor - Total Transmittance
parameter | value | unit
Total floor transmittance | 0.281 | W/m2K
Attic - Heat Dispersion
group | room | base area m2 | phi slab W
Central apartments (x4) | Living room | 29.19 | 198.8
Central apartments (x4) | Kitchen | 11.25 | 76.6
Central apartments (x4) | Bedroom 1 | 10.76 | 73.3
Central apartments (x4) | Bedroom 2 | 13.65 | 93
Central apartments (x4) | Bathroom | 10.76 | 73.3
Central apartments (x4) | TOTAL (1 apt) | 75.61 | 515
Central apartments (x4) | TOTAL centrals x4 |  | 2060
Corner apartments (x4) | Living room | 31.62 | 215.3
Corner apartments (x4) | Kitchen | 11.19 | 76.2
Corner apartments (x4) | Bedroom 1 | 11.19 | 76.2
Corner apartments (x4) | Bedroom 2 | 12.43 | 84.6
Corner apartments (x4) | Bathroom | 10.76 | 73.3
Corner apartments (x4) | TOTAL (1 apt) | 77.19 | 525.6
Corner apartments (x4) | TOTAL corners x4 |  | 2102.4
Attic - Total Dispersion
parameter | value | unit | note
Total attic dispersion | 4162.4 | kW | as reported in original report - order of magnitude suggests this may actually be W; kept as in source, verify before reuse
Attic reference temperature | -2.7 | C | per UNI 7357, non-plafonated attic with sealed tiles
Basement - Heat Dispersion
group | room | base area m2 | phi W
Corner apartments (4 units) | Living room | 31.62 | 81.9
Corner apartments (4 units) | Kitchen | 11.19 | 28
Corner apartments (4 units) | Bedroom 1 | 11.19 | 28
Corner apartments (4 units) | Bedroom 2 | 12.43 | 31.1
Corner apartments (4 units) | Bathroom | 10.76 | 26
Corner apartments (4 units) | TOTAL | 77.19 | 195
Corner apartments (4 units) | TOTAL x2 |  | 390.1
Central apartments | Living room | 29.19 | 159.1
Central apartments | Kitchen | 11.25 | 61.3
Central apartments | Bedroom 1 | 10.76 | 58.6
Central apartments | Bedroom 2 | 13.65 | 74.4
Central apartments | Bathroom | 10.76 | 58.6
Central apartments | TOTAL (1 apt) | 75.61 | 412
Central apartments | TOTAL centrals x4 |  | 1648
Basement - Total Dispersion
parameter | value | unit | note
Total basement dispersion | 2038.1 | kW | as reported in original report - order of magnitude suggests this may actually be W; kept as in source, verify before reuse
Basement reference temperature | -1.8 | C | per UNI 7357, cellar with closed windows
Ventilation & Thermal Bridges - by Apartment
apartment | room | base area m2 | volume m3 | air change rate vol h | ventilation flow kg s | phi vent W | phi thermal bridges W
South apartment | Bedroom 1 | 24.2 | 57.2 | 8.2 | 0.08 | 245.4 | 26.2
South apartment | Bathroom | 19.2 | 26.4 | 2 | 0.14 | 386.2 | 0
South apartment | Bedroom 2 | 12 | 36 | 8.2 | 0.06 | 178.4 | 18.2
South apartment | Living room | 24 | 72 | 8.2 | 0.12 | 341.4 | 21.4
South apartment | Kitchen | 18.2 | 39.2 | 1 | 0.11 | 297 | 27.2
South apartment | Corridor | 10.2 | 31 | 8.2 | 0.04 | 104.1 | 0
South apartment | TOTAL | 107.8 | 261.8 |  | 0.55 | 1552.5 | 93
South apartment | TOTAL SOUTH |  |  |  |  | 3105 | 186
North apartment | Bedroom 1 | 24.2 | 57.2 | 8.2 | 0.08 | 245.4 | 25.2
North apartment | Bathroom | 19.2 | 26.4 | 2 | 0.14 | 386.2 | 0
North apartment | Bedroom 2 | 12 | 36 | 8.2 | 0.06 | 178.4 | 22.2
North apartment | Living room | 24 | 72 | 8.2 | 0.12 | 341.4 | 26
North apartment | Kitchen | 18.2 | 39.2 | 1 | 0.11 | 297 | 29.4
North apartment | Corridor | 10.2 | 31 | 8.2 | 0.04 | 104.1 | 0
North apartment | TOTAL | 107.8 | 261.8 |  | 0.55 | 1552.5 | 102.6
North apartment | TOTAL NORTH |  |  |  |  | 3105 | 205.2
South-East apartment | Bedroom 1 | 24.2 | 57.2 | 8.2 | 0.08 | 245.4 | 46.4
South-East apartment | Bathroom | 19.2 | 26.4 | 2 | 0.14 | 386.2 | 0
South-East apartment | Bedroom 2 | 12 | 36 | 8.2 | 0.06 | 178.4 | 21.2
South-East apartment | Living room | 24 | 72 | 8.2 | 0.12 | 341.4 | 23.4
South-East apartment | Kitchen | 18.2 | 39.2 | 1 | 0.11 | 297 | 29.2
South-East apartment | Corridor | 10.2 | 31 | 8.2 | 0.04 | 104.1 | 0
South-East apartment | TOTAL | 107.8 | 261.8 |  | 0.55 | 1552.5 | 120.2
South-East apartment | TOTAL SE/SW |  |  |  |  | 3105 | 240.4
North-West apartment | Bedroom 1 | 24.2 | 57.2 | 8.2 | 0.08 | 245.4 | 51.2
North-West apartment | Bathroom | 19.2 | 26.4 | 2 | 0.14 | 386.2 | 0
North-West apartment | Bedroom 2 | 12 | 36 | 8.2 | 0.06 | 178.4 | 21.2
North-West apartment | Living room | 24 | 72 | 8.2 | 0.12 | 341.4 | 23.4
North-West apartment | Kitchen | 18.2 | 39.2 | 1 | 0.11 | 297 | 29.2
North-West apartment | Corridor | 10.2 | 31 | 8.2 | 0.04 | 104.1 | 0
North-West apartment | TOTAL | 107.8 | 261.8 |  | 0.55 | 1552.5 | 125
North-West apartment | TOTAL NW/NE |  |  |  |  | 3105 | 250
Envelope Dispersion - Grand Totals
parameter | value | unit
Opaque surfaces | 1535.8 | kW (as in source; possibly W)
Glazed surfaces | 1600.8 | kW (as in source; possibly W)
Attic | 4162.4 | kW (as in source; possibly W)
Basement | 2038.1 | kW (as in source; possibly W)
Thermal bridges | 881.6 | W
Ventilation | 12420 | kW (as in source; possibly W)
Total dispersed power (whole building) | 27685.52 | W

## Total Loads
Total Thermal Loads by Room
apartment | room | phi attic kW | phi floor kW | phi opaque kW | phi glazed kW | phi vent kW | phi thermal bridges kW | phi total W
South | Bedroom 1 | 1.667 | 1.667 | 1.501 | 1.25 | 9.686 | 0.785 | 16500
South | Bathroom | 4.167 | 4.167 | 3.051 | 2.083 | 15.935 | 0 | 29375
South | Bedroom 2 | 3.333 | 3.333 | 3.344 | 2.083 | 7.044 | 0.639 | 19750
South | Living room | 6.25 | 6.25 | 5.793 | 4.167 | 14.061 | 0.84 | 37333
South | Kitchen | 0.833 | 0.833 | 1.172 | 0.833 | 12.3 | 0.639 | 16583
South | Corridor | 0 | 0 | 0 | 0 | 4.222 | 0 | 4222
South | TOTAL | 16.25 | 16.25 | 14.863 | 10.417 | 63.248 | 2.903 | 123763
South | TOTAL SOUTH APT x2 | 32.5 | 32.5 | 29.725 | 20.833 | 126.496 | 5.806 | 247526
North | Bedroom 1 | 1.667 | 1.667 | 1.356 | 1.25 | 9.686 | 0.931 | 16500
North | Bathroom | 4.167 | 4.167 | 3.051 | 2.083 | 15.935 | 0 | 29375
North | Bedroom 2 | 3.333 | 3.333 | 3.217 | 2.083 | 7.044 | 0.767 | 19750
North | Living room | 6.25 | 6.25 | 5.625 | 4.167 | 14.061 | 1.008 | 37333
North | Kitchen | 0.833 | 0.833 | 1.05 | 0.833 | 12.3 | 0.761 | 16583
North | Corridor | 0 | 0 | 0 | 0 | 4.222 | 0 | 4222
North | TOTAL | 16.25 | 16.25 | 14.299 | 10.417 | 63.248 | 3.467 | 123763
North | TOTAL NORTH APT x2 | 32.5 | 32.5 | 28.597 | 20.833 | 126.496 | 6.933 | 247526
South-East / South-West | Bedroom 1 | 3.333 | 3.333 | 3.043 | 1.667 | 9.686 | 1.882 | 22917
South-East / South-West | Bathroom | 4.167 | 4.167 | 7.01 | 4.167 | 15.935 | 0 | 35417
South-East / South-West | Bedroom 2 | 6.25 | 6.25 | 4.719 | 4.167 | 7.044 | 0.764 | 29167
South-East / South-West | Living room | 8.333 | 8.333 | 10.043 | 8.333 | 14.061 | 0.924 | 50000
South-East / South-West | Kitchen | 3.333 | 3.333 | 1.589 | 1.667 | 12.3 | 0.722 | 22917
South-East / South-West | Corridor | 0 | 0 | 0 | 0 | 4.222 | 0 | 4222
South-East / South-West | TOTAL | 25.417 | 25.417 | 26.404 | 20 | 63.248 | 4.292 | 164638
South-East / South-West | TOTAL SE-SW APT x2 | 50.833 | 50.833 | 52.808 | 40 | 126.496 | 8.583 | 329276
North-East / North-West | Bedroom 1 | 3.333 | 3.333 | 2.939 | 1.667 | 9.686 | 2.014 | 22917
North-East / North-West | Bathroom | 4.167 | 4.167 | 7.01 | 4.167 | 15.935 | 0 | 35417
North-East / North-West | Bedroom 2 | 6.25 | 6.25 | 4.719 | 4.167 | 7.044 | 0.764 | 29167
North-East / North-West | Living room | 8.333 | 8.333 | 10.043 | 8.333 | 14.061 | 0.924 | 50000
North-East / North-West | Kitchen | 3.333 | 3.333 | 1.589 | 1.667 | 12.3 | 0.722 | 22917
North-East / North-West | Corridor | 0 | 0 | 0 | 0 | 4.222 | 0 | 4222
North-East / North-West | TOTAL | 25.417 | 25.417 | 26.3 | 20 | 63.248 | 4.424 | 164638
North-East / North-West | TOTAL NE-NW APT x2 | 50.833 | 50.833 | 52.6 | 40 | 126.496 | 8.847 | 329276
Building Total Power
parameter | value | unit
Total dispersed power - whole building | 27685.52 | W
Design thermal load Phi_d | 27.69 | kW

## Distribution Network
Radiator Model - Reference Data
parameter | value | unit
Model | TEMA 4/681
Height | 686 | mm
Center-to-center distance | 623 | mm
Depth | 128 | mm
Pitch | 60 | mm
Water content | 0.97 | L
Weight | 7.5 | kg
Heat output (deltaT=50C) | 112.1 | W per element
Distribution Network - Design Parameters
parameter | value | unit
Heating fluid | Water
Specific heat cH2O | 4186 | J/(kg K)
Supply temperature | 76 | C
Return temperature | 64 | C
Delta T | 12 | C
Target pipe velocity | 1 | m/s
Pipe Sizing by Room
apartment | room | phi total W | room mass flow kg s | pipe section area m2 | ideal diameter mm | standardized diameter mm | average pipe velocity m s | number of elements
South | Bedroom 1 | 16.5 | 0.0056 | 0.0056 | 0.1388 | 4 | 0.4354 | 4
South | Bathroom | 29.38 | 0.0097 | 0.0097 | 0.1826 | 5 | 0.4965 | 7
South | Bedroom 2 | 19.75 | 0.0063 | 0.0063 | 0.1576 | 4 | 0.5215 | 5
South | Living room | 37.33 | 0.0125 | 0.0125 | 0.2201 | 6 | 0.4382 | 8
South | Kitchen | 16.58 | 0.0056 | 0.0056 | 0.1375 | 4 | 0.4375 | 4
South | Corridor | 4.22 | 0.0014 | 0.0014 | 0.0833 | 3 | 0.1972 | 1
South | TOTAL | 123.76 | 0.041 | 0.041 | 0.9181 | 26 | 2.5264
North | Bedroom 1 | 16.5 | 0.0056 | 0.0056 | 0.1388 | 4 | 0.4354 | 4
North | Bathroom | 29.38 | 0.0097 | 0.0097 | 0.1826 | 5 | 0.4965 | 7
North | Bedroom 2 | 19.75 | 0.0063 | 0.0063 | 0.1576 | 4 | 0.5215 | 5
North | Living room | 37.33 | 0.0125 | 0.0125 | 0.2201 | 6 | 0.4382 | 8
North | Kitchen | 16.58 | 0.0056 | 0.0056 | 0.1375 | 4 | 0.4375 | 4
North | Corridor | 4.22 | 0.0014 | 0.0014 | 0.0833 | 3 | 0.1972 | 1
North | TOTAL | 123.76 | 0.041 | 0.041 | 0.9181 | 26 | 2.5264
South-West / South-East | Bedroom 1 | 22.92 | 0.0076 | 0.0076 | 0.1757 | 4 | 0.6049 | 5
South-West / South-East | Bathroom | 35.42 | 0.0118 | 0.0118 | 0.2111 | 5 | 0.5986 | 8
South-West / South-East | Bedroom 2 | 29.17 | 0.0097 | 0.0097 | 0.1813 | 5 | 0.4931 | 7
South-West / South-East | Living room | 50 | 0.0167 | 0.0167 | 0.2438 | 6 | 0.5868 | 11
South-West / South-East | Kitchen | 22.92 | 0.0076 | 0.0076 | 0.1757 | 4 | 0.6049 | 5
South-West / South-East | Corridor | 4.22 | 0.0014 | 0.0014 | 0.0833 | 3 | 0.1972 | 1
South-West / South-East | TOTAL | 164.64 | 0.0549 | 0.0549 | 1.0708 | 27 | 3.0854
North-West / North-East | Bedroom 1 | 22.92 | 0.0076 | 0.0076 | 0.1757 | 4 | 0.6049 | 5
North-West / North-East | Bathroom | 35.42 | 0.0118 | 0.0118 | 0.2111 | 5 | 0.5986 | 8
North-West / North-East | Bedroom 2 | 29.17 | 0.0097 | 0.0097 | 0.1813 | 5 | 0.4931 | 7
North-West / North-East | Living room | 50 | 0.0167 | 0.0167 | 0.2438 | 6 | 0.5868 | 11
North-West / North-East | Kitchen | 22.92 | 0.0076 | 0.0076 | 0.1757 | 4 | 0.6049 | 5
North-West / North-East | Corridor | 4.22 | 0.0014 | 0.0014 | 0.0833 | 3 | 0.1972 | 1
North-West / North-East | TOTAL | 164.64 | 0.0549 | 0.0549 | 1.0708 | 27 | 3.0854

## Pump Head
Distributed Head Losses
apartment | room | supply length m | return length m | room mass flow kg s | diameter mm | average velocity m s | reynolds number | relative roughness | friction factor | distributed pipe losses Pa
South apartment | Bedroom 1 | 7.24 | 6.74 | 0.008 | 5 | 0.39 | 4106 | 0.004 | 0.048 | 6496
South apartment | Bathroom | 13.02 | 13.05 | 0.014 | 4 | 1.137 | 9565 | 0.005 | 0.039 | 66524
South apartment | Bedroom 2 | 6.85 | 6.98 | 0.009 | 4 | 0.735 | 6184 | 0.005 | 0.043 | 16301
South apartment | Living room | 7.81 | 7.83 | 0.017 | 6 | 0.629 | 7947 | 0.003 | 0.038 | 19280
South apartment | Kitchen | 8.65 | 8.47 | 0.008 | 5 | 0.395 | 4161 | 0.004 | 0.048 | 6271
South apartment | Primary (main) | 13.35 | 13.35 | 0.056 | 12 | 0.501 | 12649 | 0.002 | 0.03 | 2026
South apartment | TOTAL | 56.92 | 56.42 | [6 empty] | 116898
North apartment | Bedroom 1 | 7.24 | 6.74 | 0.008 | 5 | 0.408 | 4297 | 0.004 | 0.047 | 6982
North apartment | Bathroom | 13.02 | 13.05 | 0.014 | 4 | 1.137 | 9565 | 0.005 | 0.039 | 66524
North apartment | Bedroom 2 | 6.85 | 6.98 | 0.009 | 4 | 0.764 | 6428 | 0.005 | 0.042 | 17351
North apartment | Living room | 8.65 | 8.47 | 0.018 | 6 | 0.642 | 8111 | 0.003 | 0.038 | 20054
North apartment | Kitchen | 8.65 | 8.47 | 0.008 | 5 | 0.411 | 4328 | 0.004 | 0.047 | 6919
North apartment | Primary (main) | 13.35 | 13.35 | 0.057 | 12 | 0.514 | 12965 | 0.002 | 0.03 | 2125
North apartment | TOTAL | 56.92 | 56.42 | [6 empty] | 119955
South-East / South-West | Bedroom 1 | 8.88 | 8.76 | 0.011 | 5 | 0.568 | 5976 | 0.004 | 0.044 | 13645
South-East / South-West | Bathroom | 10.12 | 10.76 | 0.017 | 4 | 1.371 | 11531 | 0.005 | 0.037 | 100412
South-East / South-West | Bedroom 2 | 11.11 | 10.96 | 0.014 | 4 | 1.129 | 9496 | 0.005 | 0.039 | 63273
South-East / South-West | Living room | 6.35 | 5.93 | 0.024 | 6 | 0.86 | 10860 | 0.003 | 0.035 | 20409
South-East / South-West | Kitchen | 7.12 | 8.87 | 0.011 | 5 | 0.568 | 5976 | 0.004 | 0.044 | 12423
South-East / South-West | Primary (main) | 14.8 | 14.8 | 0.077 | 12 | 0.69 | 17409 | 0.002 | 0.029 | 4001
South-East / South-West | TOTAL | 58.38 | 60.08 | [6 empty] | 214163
North-East / North-West | Bedroom 1 | 8.88 | 8.76 | 0.011 | 5 | 0.568 | 5976 | 0.004 | 0.044 | 13645
North-East / North-West | Bathroom | 10.12 | 10.76 | 0.017 | 4 | 1.371 | 11531 | 0.005 | 0.037 | 100412
North-East / North-West | Bedroom 2 | 11.11 | 10.96 | 0.014 | 4 | 1.129 | 9496 | 0.005 | 0.039 | 63273
North-East / North-West | Living room | 6.35 | 5.93 | 0.024 | 6 | 0.86 | 10860 | 0.003 | 0.035 | 20409
North-East / North-West | Kitchen | 7.12 | 8.87 | 0.011 | 5 | 0.568 | 5976 | 0.004 | 0.044 | 12423
North-East / North-West | Primary (main) | 14.8 | 14.8 | 0.077 | 12 | 0.69 | 17409 | 0.002 | 0.029 | 4001
North-East / North-West | TOTAL | 58.38 | 60.08 | [6 empty] | 214163
Localized Losses - Bends
apartment | room | number of bends | bend loss coefficient beta | localized bend losses Pa
South | Bedroom 1 | 3 | 1.9 | 426.1
South | Bathroom | 6 | 2 | 7624.9
South | Bedroom 2 | 5 | 2 | 2655.2
South | Living room | 2 | 1.8 | 699.8
South | Kitchen | 3 | 1.9 | 437
South | Primary (main) | 5 | 1.5 | 925.3
South | TOTAL | 24 |  | 12768.3
North | Bedroom 1 | 3 | 1.9 | 466.4
North | Bathroom | 6 | 2 | 7624.9
North | Bedroom 2 | 5 | 2 | 2868.8
North | Living room | 2 | 1.8 | 729.1
North | Kitchen | 3 | 1.9 | 473.2
North | Primary (main) | 5 | 1.5 | 973.9
North | TOTAL | 24 |  | 13136.3
South-East / South-West | Bedroom 1 | 3 | 1.9 | 903.4
South-East / South-West | Bathroom | 6 | 2 | 11085.6
South-East / South-West | Bedroom 2 | 4 | 2 | 5011.2
South-East / South-West | Living room | 5 | 1.8 | 3271.5
South-East / South-West | Kitchen | 5 | 1.9 | 1505.7
South-East / South-West | Primary (main) | 3 | 1.5 | 1053
South-East / South-West | TOTAL | 26 |  | 22830.4
North-East / North-West | Bedroom 1 | 3 | 1.9 | 903.4
North-East / North-West | Bathroom | 6 | 2 | 11085.6
North-East / North-West | Bedroom 2 | 4 | 2 | 5011.2
North-East / North-West | Living room | 5 | 1.8 | 3271.5
North-East / North-West | Kitchen | 5 | 1.9 | 1505.7
North-East / North-West | Primary (main) | 3 | 1.5 | 1053
North-East / North-West | TOTAL | 26 |  | 22830.4
Radiator Head Losses
room | south Pa | north Pa | se sw Pa | ne nw Pa
Bedroom 1 | 224.3 | 245.4 | 475.7 | 475.7
Bathroom | 1906.2 | 1906.2 | 2771.5 | 2771.5
Bedroom 2 | 796.5 | 860.7 | 1879.4 | 1879.4
Living room | 583.2 | 607.8 | 1090.5 | 1090.5
Kitchen | 230 | 249 | 475.7 | 475.7
Total Head Losses
room | south Pa | north Pa | se sw Pa | ne nw Pa
Bedroom 1 | 7146.4 | 7693.8 | 15024.1 | 15024.1
Bathroom | 76055.1 | 76055.1 | 114269.1 | 114269.1
Bedroom 2 | 19752.7 | 21080.5 | 70163.6 | 70163.6
Living room | 20563 | 21390.9 | 24771 | 24771
Kitchen | 6938 | 7641.2 | 14404.4 | 14404.4
Primary (main) | 2951.3 | 3098.9 | 5054 | 5054
TOTAL | 133406.5 | 136960.4 | 243686.2 | 243686.2
Pump Selection
parameter | value | unit
Most unfavorable point | Bathroom - North-West apartment
Required head loss | 128.398 | kPa
Required flow rate | 0.568 | L/s
Selected pump model | Grundfos CR 3-5 A-A-A-V-HQQV
Operating flow rate Q | 2.092 | m3/h
Operating head H | 17.63 | m
Pump efficiency | 52.8 | %
Pump+motor efficiency | 39 | %
Absorbed power P1 | 257.1 | W
Shaft power P2 | 190 | W
NPSH | 1.22 | m

## Heat Generator
Generator Selection
parameter | value | unit
Selected generator | Viessmann Vitodens 200-W (condensing wall-hung boiler)
Nominal useful power | 32 | kW
Minimum modulated power | 1.9 | kW
Efficiency at full load | 98.2 | %
Efficiency at partial load | 109.6 | %
Modulation ratio | 1:20
Required generator power (Phi_gen > 1.15 x Phi_d) | 31.84 | kW
Design thermal load Phi_d | 27.69 | kW
Generator Performance Summary
description | relative power pct | useful power W | efficiency | absorbed power W | losses W
Nominal boiler power | 100 | 32000 | 0.982 | 32587 | 587
Power required by building | 86.5 | 27132 | 0.98 | 27686 | 554

## Chimney Sizing
Chimney - Design Inputs
parameter | value | unit
Chimney height z | 7.5 | m
Flue gas mass flow Gf | 0.0152 | kg/s
Flue gas inlet temperature Tin | 465.8 | K
Flue gas outlet temperature Tout | 433.46 | K
Mean flue gas temperature Tm | 449.4 | K
Heat transfer coefficient (double-wall insulated stainless flue) U | 0.943 | W/m2K
Flue gas specific heat cp | 1.005 | kJ/(kg K)
External average seasonal temperature Te | 278 | K
External air density rho_e | 1.31 | kg/m3
Mean flue gas density rho_f | 0.7837 | kg/m3
Chimney - Geometry
parameter | value | unit
Flue gas velocity w | 2.0 | m/s
Internal cross-section S | 0.008 | m2
Internal diameter D | 0.11 | m
Heat exchange surface A | 2.59 | m2
Material | Stainless steel 316L
Type | Insulated double-wall
Chimney - Draft Verification
parameter | value | unit
Static draft Ps | 38.2 | Pa
Distributed losses dPd | 5.25 | Pa
Localized losses dPl | 5.25 | Pa
Net draft P_netto | 27.7 | Pa
Result | Positive net draft - natural draft is sufficient; no forced draft device required
Combustion & Flue Gas Flow Rates
parameter | symbol | value | unit
Absorbed power | Phi_ass | 31012 | W
Fuel volumetric flow rate | Qc | 3.12 | Sm3/h
Combustion air volumetric flow rate | Q_aria | 34.17 | m3/h
Fuel mass flow rate | Gc | 0.000596 | kg/s
Air mass flow rate | G_aria | 0.01139 | kg/s
Flue gas mass flow rate | Gf | 0.012 | kg/s

## Sources
References
Standards and calculation methods
UNI EN 12831-1:2018 - Energy performance of buildings, method for calculation of the design heat load
UNI EN ISO 6946 - Thermal resistance and thermal transmittance of building components
UNI 10349 - External design climatic conditions
UNI 5364 - Internal design temperature
UNI 7357 - Design heat load for unheated spaces (attic, basement)
Italian Ministerial Decree 05/07/1975 - Minimum glazing / natural lighting requirements
Italian Law 90/2013 - Flue gas discharge requirements for heating systems
Manufacturer technical data
Radiators: Tema 4/681 cast-iron radiator series
Circulation pump: Grundfos CR 3-3 / CR 3-5 multistage centrifugal pump
Heat generator: Viessmann Vitodens 200-W condensing wall-hung boiler
Windows: Oknoplast Winergetic Premium Passive
Other
ANIT - building material thermophysical properties database
CTI (Comitato Termotecnico Italiano) - technical/regulatory documentation for building energy design